## Digital IO
Input Signal | Bit | Location | Source | Destination | module/slot/channel | Action | NOTES | Active
Global Interlock status | 1 | Safety panel | Pilz relay | 469D Input | 494.72/01/01 | Indicate
Safety panel PLC watchdog status | 2 | Safety panel | Brentek watchdog | 469D Input | 494.72/01/02 | Indicate | hardware interlock
Watchdog pulse | 1 | 469D Output | Controller | Safety Panel | 494.72/01/01
Signal | Bit | Location | Source | Destination | module/slot/channel | Action | NOTES | Active
Wago 750-610 +24V fault | 1 | Console | Safety Panel Wago | Safety PLC Input | 750-610/02/01 | Interlock
Wago 750-610 fuse fault | 2 | Console | Safety Panel Wago | Safety PLC Input | 750-620/02/02 | Interlock
ESTOP desktop status | 3 | Control room | desktop box | Safety PLC Input | 750-432/05/01 | Display | Status Panel Indicator
ESTOP pump room status | 4 | Pump room | wall mount box | Safety PLC Input | 750-432/05/02 | Display | Status Panel Indicator
ESTOP pit east status | 5 | Pit | wall mount box (east) | Safety PLC Input | 750-432/05/03 | Display | Status Panel Indicator
ESTOP pit west status | 6 | Pit | wall mount box (west) | Safety PLC Input | 750-432/05/04 | Display | Status Panel Indicator
PowerPC watchdog status | 7 | Safety panel | Brentek watchdog | Safety PLC Input | 750-432/06/01 | Indicate | hardware interlock
Controller UPS on battery | 8 | Control room | Controller UPS | Safety PLC Input | 750-432/06/02 | Indicate/Interlock (??) | Inhibit HSM ON if not ON. If HSM ON and FG running, generate interlock(??)
Controller UPS battery low | 9 | Control room | Controller UPS | Safety PLC Input | 750-432/06/03 | Indicate/Abort (??) | Inhibit HSM ON if not on. If HSM ON and running, Indicate OR abort(??)
Controller UPS internal fault | 10 | Control room | Controller UPS | Safety PLC Input | 750-432/06/04 | Indicate | Inhibit HSM ON
Controller UPS replace battery | 11 | Control room | Controller UPS | Safety PLC Input | 750-432/07/01 | Indicate | Inhibit HSM ON
Sump overlevel | 12 | Pit | Sump Float Switch | Safety PLC Input | 750-432/07/02 | (??) | Ask Kiyo/Customer
Sump pump running | 13 | Pit | Sump Running Contact | Safety PLC Input | 750-432/07/03 | Display | Status Panel Indicator
HPC controller watchdog status | 14 | Pump room | Brentek watchdog | Safety PLC Input | 750-432/07/04 | Indicate | hardware interlock
Pilot pressure low | 15 | Pit | Hsm | Safety PLC Input | 750-432/08/01 | Interlock
Pilot filter dirty | 16 | Pit | Hsm | Safety PLC Input | 750-432/08/02 | Indicate
Desktop Abort | 17 | Control room | Desktop Abort box | Safety PLC Input | 750-432/08/03 | Abort | only use 1 N/C contact
Test cell Abort | 18 | Test cell | Remote Abort box | Safety PLC Input | 750-432/08/04 | Abort | only use 1 N/C contact
Pit Abort | 19 | Pit | Wall Mount Abort box | Safety PLC Input |  | Abort | only use 1 N/C contact
Watchdog pulse | 1 | Safety Panel | Safety Panel Wago | Brentek watchdog | 750-502/09/01
Spare Digital Output | 2 | Safety Panel |  |  | 750-502/09/02
Signal |  | Location | Source | Destination | module/slot/channel | Action | NOTES | Active
Wago 750-610 +24V fault | 1 | HPC Panel | internal | HPC PLC Input | 750-610/02/1 | Interlock
Wago 750-610 fuse fault | 2 | HPC Panel | internal | HPC PLC Input | 750-610/02/2 | Interlock
HPU #1 Running | 3 | HPC Panel | TBx1 | HPC PLC Input | 750-401/03/1
HPU #1 Low Level | 4 | HPC Panel |  | HPC PLC Input | 750-401/03/2
HPU #1 Over Temp | 5 | HPC Panel |  | HPC PLC Input | 750-401/03/3
HPU #1 Dirty Filter | 6 | HPC Panel |  | HPC PLC Input | 750-401/03/4
HPU #2 Running | 7 | HPC Panel |  | HPC PLC Input | 750-401/04/1
HPU #2 Low Level | 8 | HPC Panel |  | HPC PLC Input | 750-401/04/2
HPU #2 Over Temp | 9 | HPC Panel |  | HPC PLC Input | 750-401/04/3
HPU #2 Dirty Filter | 10 | HPC Panel |  | HPC PLC Input | 750-401/04/4
HPU #3 Running | 11 | HPC Panel |  | HPC PLC Input | 750-401/05/1
HPU #3 Low Level | 12 | HPC Panel |  | HPC PLC Input | 750-401/05/2
HPU #3 Over Temp | 13 | HPC Panel |  | HPC PLC Input | 750-401/05/3
HPU #3 Dirty Filter | 14 | HPC Panel |  | HPC PLC Input | 750-401/05/4
HPU #4 Running | 15 | HPC Panel |  | HPC PLC Input | 750-401/06/1
HPU #4 Low Level | 16 | HPC Panel |  | HPC PLC Input | 750-401/06/2
HPU #4 Over Temp | 17 | HPC Panel |  | HPC PLC Input | 750-401/06/3
HPU #4 Dirty Filter | 18 | HPC Panel |  | HPC PLC Input | 750-401/06/4
HPU #5 Running | 19 | HPC Panel |  | HPC PLC Input | 750-401/07/1
HPU #5 Low Level | 20 | HPC Panel |  | HPC PLC Input | 750-401/07/2
HPU #5 Over Temp | 21 | HPC Panel |  | HPC PLC Input | 750-401/07/3
HPU #5 Dirty Filter | 22 | HPC Panel |  | HPC PLC Input | 750-401/07/4
HPU #6 Running | 23 | HPC Panel |  | HPC PLC Input | 750-401/08/1
HPU #6 Low Level | 24 | HPC Panel |  | HPC PLC Input | 750-401/08/2
HPU #6 Over Temp | 25 | HPC Panel |  | HPC PLC Input | 750-401/08/3
HPU #6 Dirty Filter | 26 | HPC Panel |  | HPC PLC Input | 750-401/08/4
HPU #7 Running | 27 | HPC Panel |  | HPC PLC Input | 750-401/09/1
HPU #7 Low Level | 28 | HPC Panel |  | HPC PLC Input | 750-401/09/2
HPU #7 Over Temp | 29 | HPC Panel |  | HPC PLC Input | 750-401/09/3
HPU #7 Dirty Filter | 30 | HPC Panel |  | HPC PLC Input | 750-401/09/4
HPC UPS on battery | 31 | Pump room | HPC UPS | HPC PLC Input | 750-432/10/1
HPC UPS battery low | 32 | Pump room | HPC UPS | HPC PLC Input | 750-432/10/2
HPC UPS internal fault | 33 | Pump room | HPC UPS | HPC PLC Input | 750-432/10/3
HPC UPS replace battery | 34 | Pump room | HPC UPS | HPC PLC Input | 750-432/10/4
Spare #1 | 35 | HPC Panel |  | HPC PLC Input | 750-432/11/1
Spare #2 | 36 | HPC Panel |  | HPC PLC Input | 750-432/11/2
Spare #3 | 37 | HPC Panel |  | HPC PLC Input | 750-432/11/3
Spare #4 | 38 | HPC Panel |  | HPC PLC Input | 750-432/11/4
Wago 750-610 +24V fault | 39 | HPC Panel | internal | HPC PLC Input | 750-610/12/1 | Interlock
Wago 750-610 fuse fault | 40 | HPC Panel | internal | HPC PLC Input | 750-610/12/2 | Interlock
HPU #1 Start | 1 | HPC Panel | HPC PLC Output | HPU #1 | 750-513/13/1
HPU #1 Run | 2 | HPC Panel | HPC PLC Output | HPU #1 | 750-513/13/2
HPU #1 High | 3 | HPC Panel | HPC PLC Output | HPU #1 | 750-513/14/1
HPU #1 Spare | 4 | HPC Panel | HPC PLC Output | HPU #1 | 750-513/14/2
HPU #2 Start | 5 | HPC Panel | HPC PLC Output | HPU #2 | 750-513/15/1
HPU #2 Run | 6 | HPC Panel | HPC PLC Output | HPU #2 | 750-513/15/2
HPU #2 High | 7 | HPC Panel | HPC PLC Output | HPU #2 | 750-513/16/1
HPU #2 Spare | 8 | HPC Panel | HPC PLC Output | HPU #2 | 750-513/16/2
HPU #3 Start | 9 | HPC Panel | HPC PLC Output | HPU #3 | 750-513/17/1
HPU #3 Run | 10 | HPC Panel | HPC PLC Output | HPU #3 | 750-513/17/2
HPU #3 High | 11 | HPC Panel | HPC PLC Output | HPU #3 | 750-513/18/1
HPU #3 Spare | 12 | HPC Panel | HPC PLC Output | HPU #3 | 750-513/18/2
HPU #4 Start | 13 | HPC Panel | HPC PLC Output | HPU #4 | 750-513/19/1
HPU #4 Run | 14 | HPC Panel | HPC PLC Output | HPU #4 | 750-513/19/2
HPU #4 High | 15 | HPC Panel | HPC PLC Output | HPU #4 | 750-513/20/1
HPU #4 Spare | 16 | HPC Panel | HPC PLC Output | HPU #4 | 750-513/20/2
HPU #5 Start | 17 | HPC Panel | HPC PLC Output | HPU #5 | 750-513/21/1
HPU #5 Run | 18 | HPC Panel | HPC PLC Output | HPU #5 | 750-513/21/2
HPU #5 High | 19 | HPC Panel | HPC PLC Output | HPU #5 | 750-513/22/1
HPU #5 Spare | 20 | HPC Panel | HPC PLC Output | HPU #5 | 750-513/23/2
HPU #6 Start | 21 | HPC Panel | HPC PLC Output | HPU #6 | 750-513/23/1
HPU #6 Run | 22 | HPC Panel | HPC PLC Output | HPU #6 | 750-513/24/2
HPU #6 High | 23 | HPC Panel | HPC PLC Output | HPU #6 | 750-513/24/1
HPU #6 Spare | 24 | HPC Panel | HPC PLC Output | HPU #6 | 750-513/25/2
HPU #7 Start | 25 | HPC Panel | HPC PLC Output | HPU #7 | 750-513/25/1
HPU #7 Run | 26 | HPC Panel | HPC PLC Output | HPU #7 | 750-513/26/2
HPU #7 High | 27 | HPC Panel | HPC PLC Output | HPU #7 | 750-513/26/1
HPU #7 Spare | 28 | HPC Panel | HPC PLC Output | HPU #7 | 750-513/13/2

## Digital Outputs
Controller Digital Output Signal | Bit | Location | module/slot/channel | Destination
PowerPC Watchdog pulse | 1 | 469D Output | 494.72/01/01 | Brentek watchdog
At Zero Position | 2 | 469D Output | 494.72/01/02
Program Running | 3 | 469D Output | 494.72/01/03
Alive indicator | 4 | 469D Output | 494.72/01/04
FACOM 10 seconds before run | 5 | 469D Output | 494.72/01/05 | Pulse 0.1 seconds Off-On-Off
FACOM Start | 6 | 469D Output | 494.72/01/06 | Pulse 0.1 seconds Off-On-Off
Safety Wago Output Signal | Bit | Location | module/slot/channel | Destination
PLC Watchdog pulse | 1 | Safety Panel | 750-502/08/01 | Brentek watchdog
Spare Digital Output | 2 | Safety Panel | 750-502/08/02
ESTOP chain trip | 3 | Safety Panel | 750-513/09/01 | 6-cond#1 ORG
Spare Digital Output | 4 | Safety Panel | 750-513/09/02
HPC Wago Output Signal | Bit | Location | module/slot/channel | Destination
HPU #1 Start | 1 | HPC Panel | 750-513/14/01 | TB3/4
HPU #1 Run | 2 | HPC Panel | 750-513/14/02 | TB3/6
HPU #1 High | 3 | HPC Panel | 750-513/15/01 | TB3/13
Spare | 4 | HPC Panel | 750-513/15/02
HPU #2 Start | 5 | HPC Panel | 750-513/16/01 | TB3/18
HPU #2 Run | 6 | HPC Panel | 750-513/16/02 | TB3/20
HPU #2 High | 7 | HPC Panel | 750-513/17/01 | TB3/27
HPU #2 /Stop | 8 | HPC Panel | 750-513/17/02
HPU #3 Start | 9 | HPC Panel | 750-513/18/01 | TB3/32
HPU #3 Run | 10 | HPC Panel | 750-513/18/02 | TB3/34
HPU #3 High | 11 | HPC Panel | 750-513/19/01 | TB3/41
HPU #3 Spare | 12 | HPC Panel | 750-513/19/02
HPU #4 Start | 13 | HPC Panel | 750-513/20/01 | TB3/46
HPU #4 Run | 14 | HPC Panel | 750-513/20/02 | TB3/48
HPU #4 High | 15 | HPC Panel | 750-513/21/01 | TB3/55
HPU #4 Spare | 16 | HPC Panel | 750-513/21/02
HPU #5 Start | 17 | HPC Panel | 750-513/22/01 | TB3/60
HPU #5 Run | 18 | HPC Panel | 750-513/22/02 | TB3/62
HPU #5 High | 19 | HPC Panel | 750-513/23/01 | TB3/69
HPU #5 Spare | 20 | HPC Panel | 750-513/23/02
HPU #6 Start | 21 | HPC Panel | 750-513/24/01 | TB3/74
HPU #6 Run | 22 | HPC Panel | 750-513/24/02 | TB3/76
HPU #6 High | 23 | HPC Panel | 750-513/25/01 | TB3/83
HPU #6 Spare | 24 | HPC Panel | 750-513/25/02
HPU #7 Start | 25 | HPC Panel | 750-513/26/01 | TB3/88
HPU #7 Run | 26 | HPC Panel | 750-513/26/02 | TB3/90
HPU #7 High | 27 | HPC Panel | 750-513/27/01 | TB3/97
HPU #7 Spare | 28 | HPC Panel | 750-513/27/02
HPC ESTOP chain closed | 29 | HPC Panel | 750-513/28/01
HPC spare | 30 | HPC Panel | 750-513/28/02
HPC Watchdog pulse | 31 | HPC Panel | 750-502/29/01
HPC spare | 32 | HPC Panel | 750-502/29/02

## Digital Inputs
Updated to Rev. E 28-OCT-2013
Controller Digital Input Signal | Bit | Location | Source | Destination | module/slot/channel | Action | NOTES
Global Interlock status | 1 | Safety panel | Pilz relay | 469D Input | 494.72/01/01 | Indicate
Safety panel PLC watchdog status | 2 | Safety panel | Brentek watchdog | 469D Input | 494.72/01/02 | Indicate | hardware interlock
Waste Oil Level warning | 3 | Safety panel | Float switch | 496D Input | 494.72/01/03 | Warning
Safety Wago Input Signal | Bit | Location | Source | Destination | module/slot/channel | Action | NOTES
Wago 750-610 +24V fault | 1 | Console | Safety Panel Wago | Safety PLC Input | 750-610/01/01 | Indicate
Wago 750-610 fuse fault | 2 | Console | Safety Panel Wago | Safety PLC Input | 750-610/01/02 | Indicate
ESTOP desktop status | 3 | Control room | desktop box | Safety PLC Input | 750-432/02/01 | Display | Status Panel Indicator
ESTOP pump room status | 4 | Pump room | wall mount box | Safety PLC Input | 750-432/02/02 | Display | Status Panel Indicator
ESTOP pit east status | 5 | Pit | wall mount box (east) | Safety PLC Input | 750-432/02/03 | Display | Status Panel Indicator
ESTOP pit west status | 6 | Pit | wall mount box (west) | Safety PLC Input | 750-432/02/04 | Display | Status Panel Indicator
PowerPC watchdog status | 7 | Safety panel | Brentek watchdog | Safety PLC Input | 750-432/03/01 | Indicate | hardware interlock
Controller UPS on battery | 8 | Control room | Controller UPS | Safety PLC Input | 750-432/03/02 | Indicate/Warn | Inhibit HSM ON if not ON. If HSM ON and FG running, just indicate.
Controller UPS battery low | 9 | Control room | Controller UPS | Safety PLC Input | 750-432/03/03 | Indicate/Interlock | Inhibit HSM ON if not on. If HSM ON and running, Interlock
Spare Input | 10 |  |  | Safety PLC Input | 750-432/03/04
Spare Input | 11 |  |  | Safety PLC Input | 750-432/04/01
Sump overlevel | 12 | Pit | Sump Float Switch | Safety PLC Input | 750-432/04/02 | Interlock | Interlock per Kiyo
Sump pump running | 13 | Pit | Sump Running Contact | Safety PLC Input | 750-432/04/03 | Display | Status Panel Indicator
HPC controller watchdog status | 14 | Pump room | Brentek watchdog | Safety PLC Input | 750-432/04/04 | Indicate | hardware interlock
Pilot pressure low | 15 | Pit | Hsm | Safety PLC Input | 750-432/05/01 | Interlock | If hydraulics ON and this goes active, Interlock
Pilot filter dirty | 16 | Pit | Hsm | Safety PLC Input | 750-432/05/02 | Indicate
Desktop Abort | 17 | Control room | Desktop Abort box | Safety PLC Input | 750-432/05/03 | Abort
Test area Abort | 18 | Test cell | Remote Abort box | Safety PLC Input | 750-432/05/04 | Abort
Spare Input | 19 |  |  | Safety PLC Input | 750-432/06/01
469D ESTOP status | 20 | Controller | 494.74 P44 | Safety PLC Input | 750-432/06/02 | Display | 469D signaling estop
HPC Interlock status | 21 | Pump room | HPC Wago | Safety PLC Input | 750-432/06/03 | Display | hardware interlock
Spare Input | 22 |  |  | Safety PLC Input | 750-432/06/04
HPC Wago Input Signal | Bit | Location | Source | Destination | module/slot/channel | Action | NOTES
Wago 750-610 +24V fault | 1 | HPC Panel | internal | HPC PLC Input | 750-610/01/01 | Indicate
Wago 750-610 fuse fault | 2 | HPC Panel | internal | HPC PLC Input | 750-610/01/02 | Indicate
HPU #1 Running | 3 | HPC Panel | TB-4 | HPC PLC Input | 750-401/02/01
HPU #1 Low Level | 4 | HPC Panel | TB-1 | HPC PLC Input | 750-401/02/02
HPU #1 Over Temp | 5 | HPC Panel | TB-9 | HPC PLC Input | 750-401/02/03
HPU #1 Dirty Filter | 6 | HPC Panel | TB-8 | HPC PLC Input | 750-401/02/04
HPU #2 Running | 7 | HPC Panel | TB-17 | HPC PLC Input | 750-401/03/01
HPU #2 Low Level | 8 | HPC Panel | TB-14 | HPC PLC Input | 750-401/03/02
HPU #2 Over Temp | 9 | HPC Panel | TB-22 | HPC PLC Input | 750-401/03/03
HPU #2 Dirty Filter | 10 | HPC Panel | TB-21 | HPC PLC Input | 750-401/03/04
HPU #3 Running | 11 | HPC Panel | TB-30 | HPC PLC Input | 750-401/04/01
HPU #3 Low Level | 12 | HPC Panel | TB-27 | HPC PLC Input | 750-401/04/02
HPU #3 Over Temp | 13 | HPC Panel | TB-35 | HPC PLC Input | 750-401/04/03
HPU #3 Dirty Filter | 14 | HPC Panel | TB-34 | HPC PLC Input | 750-401/04/04
HPU #4 Running | 15 | HPC Panel | TB-43 | HPC PLC Input | 750-401/05/01
HPU #4 Low Level | 16 | HPC Panel | TB-40 | HPC PLC Input | 750-401/05/02
HPU #4 Over Temp | 17 | HPC Panel | TB-48 | HPC PLC Input | 750-401/05/03
HPU #4 Dirty Filter | 18 | HPC Panel | TB-47 | HPC PLC Input | 750-401/05/04
HPU #5 Running | 19 | HPC Panel | TB-56 | HPC PLC Input | 750-401/06/01
HPU #5 Low Level | 20 | HPC Panel | TB-53 | HPC PLC Input | 750-401/06/02
HPU #5 Over Temp | 21 | HPC Panel | TB-61 | HPC PLC Input | 750-401/06/03
HPU #5 Dirty Filter | 22 | HPC Panel | TB-60 | HPC PLC Input | 750-401/06/04
HPU #6 Running | 23 | HPC Panel | TB-69 | HPC PLC Input | 750-401/07/01
HPU #6 Low Level | 24 | HPC Panel | TB-66 | HPC PLC Input | 750-401/07/02
HPU #6 Over Temp | 25 | HPC Panel | TB-74 | HPC PLC Input | 750-401/07/03
HPU #6 Dirty Filter | 26 | HPC Panel | TB-73 | HPC PLC Input | 750-401/07/04
HPU #7 Running | 27 | HPC Panel | TB-82 | HPC PLC Input | 750-401/08/01
HPU #7 Low Level | 28 | HPC Panel | TB-79 | HPC PLC Input | 750-401/08/02
HPU #7 Over Temp | 29 | HPC Panel | TB-87 | HPC PLC Input | 750-401/08/03
HPU #7 Dirty Filter | 30 | HPC Panel | TB-86 | HPC PLC Input | 750-401/08/04
HPC UPS on battery | 31 | Pump room | HPC UPS | HPC PLC Input | 750-432/09/01 | Indicate/Warn | Inhibit HSM ON if ON. If HSM ON and FG running, just indicate.
HPC UPS battery low | 32 | Pump room | HPC UPS | HPC PLC Input | 750-432/09/02 | Indicate/Interlock | Inhibit HSM ON if on. If HSM ON and running, Interlock.
Spare Input | 33 |  |  |  | 750-432/09/03
Spare Input | 34 |  |  |  | 750-432/09/04
Spare Input | 35 | HPC Panel |  | HPC PLC Input | 750-432/10/01
SAFETY Panel signaling I/L | 36 | HPC Panel | Safety panel | HPC PLC Input | 750-432/10/02
Spare #3 | 37 | HPC Panel |  | HPC PLC Input | 750-432/10/03
Spare #4 | 38 | HPC Panel |  | HPC PLC Input | 750-432/10/04
Wago 750-610 +24V fault | 39 | HPC Panel | internal | HPC PLC Input | 750-610/11/01 | Indicate
Wago 750-610 fuse fault | 40 | HPC Panel | internal | HPC PLC Input | 750-610/11/02 | Indicate

## Analog Inputs
Safety Wago Input Signal | Word | Location | Source | Destination | module/slot/channel | NOTES
spare 4-20 ma | 1 |  |  |  | 750-455/07/01
Return oil temperature | 2 | Pit | Temperature Sensor | Safety Wago Ain | 750-455/07/02 | Via sandwich plate in return line.
spare 4-20 ma | 3 |  |  |  | 750-455/07/03
spare 4-20 ma | 4 |  |  |  | 750-455/07/04
HPC Wago Input Signal | Word | Location | Source | Destination | module/slot/channel | NOTES
HPS #2 Reservoir level | 1 | Pump Room | Float sensor in HPS #2 | HPC Wago Ain | 750-455/11/01
spare 4-20 ma | 2 |  |  |  | 750-455/11/02
spare 4-20 ma | 3 |  |  |  | 750-455/11/03
spare 4-20 ma | 4 |  |  |  | 750-455/11/04
HPS #2 Temp | 5 | Pump Room | RTD Temp Sensor in HPS #2 | HPC Wago Ain | 750-461/12/01
Spare RTD input | 6 |  |  |  | 750-461/12/02
NOTE:
User Duc #1 has been dedicated to system pressure.